## guardTest
basicHotAbsoluteGuardInputs | values | deadSensorGuardInputs | values | hotGuardTestInputs | values | guardOrderMIXInputs | values
num_guard_units | 1 | ds_num_guard_units_value | 1 | config_allow_num_exceedences_guard_initial | 1 | fan_ctlr_min_value | 50
num_minutes_guard_timer | 3 | ds_num_minutes_guard_timer_value | 2 | config_allow_num_exceedences_guard_value2 | 2 | fan_ctrl_max_value | 100
percent_deadsensor_threshold | 100 | ds_percent_dead_sensor_threshold_default_value | 30 | group_allow_num_exceedences_guard_value0 | 0 | allow_num_exceedences_guard_cleanup_value | 9
num_minutes_past | 5 | ds_num_minutes_past_value | 2 | group_allow_num_exceedences_guard_value1 | 1 | guard_hot_abs_temp_cleanup_value | 95
allow_num_exceedences_control_initial | 10 | dead_sensor_test_temp | 66 | group_allow_num_exceedences_guard_value2 | 2 | allow_num_exceedences_control_cleanup_value | 9
allow_num_exceedences_guard_initial | 10 | alarm_dead_sensor_hysteresis_cleanup_value | 0 | config_CAT_guard_band_range_initial | 4 | guard_hot_abs_temp_intial | 99
alm_hot_abs_temp_initial | 200 | alarm_dead_sensor_threshold_cleanup_value | 0 | config_CAT_guard_band_range_value5 | 5 | rack_temp | 66
guard_hot_abs_temp_intial | 90 | control_dead_sensor_threshold_cleanup_value | 0 | config_num_guard_units_value1 | 1 | high_set_point_limit | 80.6
allow_num_exceedences_control_default | 0 | dead_sensor_alarm_count | 1 | config_num_guard_units_value2 | 2 | high_set_point_limit_cleanup | 88
allow_num_exceedences_guard_default | 1 | guard_on | GUARD_ON | config_num_minutes_guard_timer_value2 | 2 | low_set_point_limit | 64.4
alm_hot_abs_temp_default | 90 | guard_off | GUARD_OFF | config_num_minutes_guard_timer_value4 | 4 | low_set_point_limit_cleanup | 60
guard_hot_abs_temp_default | 90 | group_dead_sensor_alarm_on | ALARM_ON | config_guard_hysteresis_band_value1 | 1 | config_num_guard_units_value | 1
percent_deadsensor_threshold_default | 30 | group_dead_sensor_alarm_off | ALARM_OFF | config_guard_hysteresis_band_value2 | 2 | config_num_minutes_guard_timer_value | 1
sensor_point_cooling_temp | 65 | control_dead_sensor_threshold_property_name | ControlDeadSensorThreshold | high_set_point_limit | 80.6 | config_system_num_minutes_past | 20
sensor_point_hot_temp | 100 | grp_dead_sensor_hysteresis_value_default_value | 10 | high_set_point_limit_cleanup | 88 | first_ahus_predicted_into_guard | CAC_16,CAC_13,CRAC_3A-02
expected_ahu_to_be_on | 4 |  |  | low_set_point_limit | 64.4 | CAC_10 | 70
|  |  |  | low_set_point_limit_cleanup | 60 | CAC_11 | 100
|  |  |  | guard_on | GUARD_ON | CAC_12 | 90
|  |  |  | guard_off | GUARD_OFF | CAC_13 | 80
|  |  |  | group_hot_alarm_on | ALARM_ON | CAC_14 | 66
|  |  |  | group_hot_alarm_off | ALARM_OFF | CAC_15 | 60
|  |  |  | allow_num_exceedences_guard_cleanup_value | 9 | CAC_16 | 50
|  |  |  | guard_hot_abs_temp_cleanup_value | 99 | CAC_17 | 75
|  |  |  | alm_hot_abs_temp_cleanup_value | 99 | CRAC_3A-01 | 100
|  |  |  | hot_guard_intial_temp_all_racks | 66 | CRAC_3A-02 | 50
[6 empty] | CRAC_3A-03 | 80
[6 empty] | CRAC_3A-04 | 70

## overrideTest
override1TestInputs | values | minOnNoBindings Test | values | minOnGeneralTest | values
guard_hot_abs_temp_intial | 99 | high_set_point_limit | 55 | high_set_point_limit | 120
fan_ctlr_min_value | 50 | low_set_point_limit | 45 | low_set_point_limit | 110
fan_ctrl_max_value | 100 | config_allow_num_exceedences_guard | 9 | config_allow_num_exceedences_guard | 9
config_num_guard_units_value | 1 | config_allow_num_exceedences_control | 0 | config_allow_num_exceedences_control | 0
config_num_minutes_guard_timer_value | 1 | grp_property_alg_name | DASHAM_MIX | grp_property_alg_name | DASHAM_MIX
config_system_num_minutes_past | 20 | config_num_minutes_start_timer | 1 | config_num_minutes_start_timer | 1
high_set_point_limit | 80.6 | rack_tempF | 50 | min_required_ahu_on_0 | 0
low_set_point_limit | 64.4 | rat_tempF | 68 | min_required_ahu_on_9 | 9
rack_temp | 66 | dat_tempF | 53 | min_required_ahu_on_2 | 2
rat_tempF | 68 | power_monitor_pwr_kW | 0.4 | guard_hot_abs_temp_default | 90
dat_tempF | 53 | min_required_ahu_on_0 | 0 | alm_hot_abs_temp_default | 90
SFCMinValue | 72 | min_required_ahu_on_9 | 9 | config_num_minutes_start_timer_default | 15
SFCMaxValue | 88 | min_required_ahu_on_2 | 2 | expected_ahu_turn_ON_order | CAC_14,CAC_13,CAC_15,CAC_17,CAC_16,CAC_12,CAC_11,CAC_10
ahu_1 | CAC_10 | guard_hot_abs_temp_default | 90 | ahu_name_0 | CAC_10
ahu_1_sfc_value | 77 | alm_hot_abs_temp_default | 90 | ahu_name_1 | CAC_11
ahu_1_bop_value | ON | config_num_minutes_start_timer_default | 15 | ahu_name_2 | CAC_12
on_value | 1 | expected_ahu_turn_ON_order | NB-AHU-14,NB-AHU-13,NB-AHU-15,NB-AHU-17,NB-AHU-16,NB-AHU-12,NB-AHU-11,NB-AHU-10 | ahu_name_3 | CAC_13
off_value | 0 | ahu_name_0 | NB-AHU-10 | ahu_name_4 | CAC_14
ahu_2 | CAC_13 | ahu_name_1 | NB-AHU-11 | ahu_name_5 | CAC_15
ahu_2_sfc_value | 79 | ahu_name_2 | NB-AHU-12 | ahu_name_6 | CAC_16
ahu_2_bop_value | AUTO | ahu_name_3 | NB-AHU-13 | ahu_name_7 | CAC_17
ahu_3 | CAC_15 | ahu_name_4 | NB-AHU-14 | CAC_10 | CHW,200000,4.13
ahu_3_sfc_value | 81 | ahu_name_5 | NB-AHU-15 | CAC_11 | CHW,190000,4.13
ahu_3_bop_value | OFF | ahu_name_6 | NB-AHU-16 | CAC_12 | CHW,180000,4.13
|  | ahu_name_7 | NB-AHU-17 | CAC_13 | DX,190000,4.13
|  |  |  | CAC_14 | DX,190000,4.16
|  |  |  | CAC_15 | DX,190000,4.12
|  |  |  | CAC_16 | DX,190000,4.08
|  |  |  | CAC_17 | DX,190000,4.09

## tuesdaysuite
testcase | runmode | command | name | reporttitle | output dir | output | environment | groupname | testname | outputxml | slash | combineoutputxml
cleanReports | yes | robot |  |  | Reports/cleanReports | cleanReports.xml | config91 |  | cleanReports.robot |  |  | basichotGuard.xml/deadSensorGuard.xml/hotGuard.xml/guardOrderMIX.xml/vxOverrideUIvalues.xml/uiPopup.xml/minOnNoBindings.xml/minOnGeneral.xml
Guard1 | yes | pabot --pabotlib --processes 2 | Guard1_Imputes-test | BasicHotAbsoluteGuard | Reports | basichotGuard.xml | config91 | Imputes-test | basicHotAbsoluteGuardTest.robot/staleStatePrevention.robot | basichotGuard.xml
Guard2 | yes | pabot --pabotlib --processes 2 | Guard2_Imputes-test | DeadSensorGuard | Reports | deadSensorGuard.xml | config91 | Imputes-test | deadSensorGuardTest.robot/staleStatePrevention.robot | deadSensorGuard.xml | /
Guard3 | yes | pabot --pabotlib --processes 2 | Guard3_General-test | HotGuard | Reports | hotGuard.xml | config91 | General-test | hotGuardTest.robot/staleStatePrevention.robot | hotGuard.xml | /
Guard4 | yes | pabot --pabotlib --processes 2 | Guard4_General-test | GuardOrderMIX | Reports | guardOrderMIX.xml | config91 | General-test | guardOrderMIXTest.robot/staleStatePrevention.robot | guardOrderMIX.xml | /
Override1 | yes | pabot --pabotlib --processes 2 | Override1_General-test | VXOverrideUIvalues | Reports | vxOverrideUIvalues.xml | config91 | General-test | vxOverrideUIvaluesTest.robot/staleStatePrevention.robot | vxOverrideUIvalues.xml | /
UITestPopup | yes | pabot --pabotlib --processes 1 | Popup | Popups | Reports | uiPopup.xml | config91 | General-test | uiPopupTest.robot | uiPopup.xml | /
Override_minOnNoBindings | yes | pabot --pabotlib --processes 2 | Override_MinOnNoBindings-test | MinOnNoBindings | Reports | minOnNoBindings.xml | config146 | NoBindings | minOnNoBindingsTest.robot/staleStatePrevention.robot | minOnNoBindings.xml | /
MinOnGeneralTest | yes | pabot --pabotlib --processes 1 | Override_MinOnGeneral-test | MinOnGeneral | Reports | minOnGeneral.xml | config146 | General-test | minOnGeneralTest.robot | minOnGeneral.xml | /
combinereport | yes | rebot --removekeywords passed | Guard_Override_Test | Test performed on environment 91 | Reports | basichotGuard.xml/deadSensorGuard.xml/hotGuard.xml/guardOrderMIX.xml/vxOverrideUIvalues.xml/uiPopup.xml/minOnNoBindings.xml/minOnGeneral.xml
moveReports | yes | robot |  |  | Reports/cleanReports | moveReports.xml | config91 |  | moveReports.robot
Note on O1: Do not change

## wednesdaysuite
testcase | runmode | command | name | reporttitle | output dir | output | environment | groupname | testname | outputxml | slash | combineoutputxml
cleanReports | yes | robot |  |  | Reports/cleanReports | cleanReports.xml | config118 |  | cleanReports.robot |  |  | basichotGuard.xml/deadSensorGuard.xml/hotGuard.xml/guardOrderMIX.xml/vxOverrideUIvalues.xml/uiPopup.xml/minOnNoBindings.xml/minOnGeneral.xml
Guard1 | yes | pabot --pabotlib --processes 2 | Guard1_RSP-test | BasicHotAbsoluteGuard | Reports | basichotGuard.xml | config37 | RSP-test | basicHotAbsoluteGuardTest.robot/staleStatePrevention.robot | basichotGuard.xml
Guard2 | yes | pabot --pabotlib --processes 2 | Guard2_Imputes-test | DeadSensorGuard | Reports | deadSensorGuard.xml | config91 | Imputes-test | deadSensorGuardTest.robot/staleStatePrevention.robot | deadSensorGuard.xml | /
Guard3 | yes | pabot --pabotlib --processes 2 | Guard3_General-test | HotGuard | Reports | hotGuard.xml | config118 | General-test | hotGuardTest.robot/staleStatePrevention.robot | hotGuard.xml | /
Guard4 | yes | pabot --pabotlib --processes 2 | Guard4_General-test | GuardOrderMIX | Reports | guardOrderMIX.xml | config118 | General-test | guardOrderMIXTest.robot/staleStatePrevention.robot | guardOrderMIX.xml | /
Override1 | yes | pabot --pabotlib --processes 2 | Override1_General-test | VXOverrideUIvalues | Reports | vxOverrideUIvalues.xml | config91 | General-test | vxOverrideUIvaluesTest.robot/staleStatePrevention.robot | vxOverrideUIvalues.xml | /
UITestPopup | yes | pabot --pabotlib --processes 1 | Popup | Popups | Reports | uiPopup.xml | config91 | General-test | uiPopupTest.robot | uiPopup.xml | /
Override_minOnNoBindings | yes | pabot --pabotlib --processes 2 | Override_MinOnNoBindings-test | MinOnNoBindings | Reports | minOnNoBindings.xml | config146 | NoBindings | minOnNoBindingsTest.robot/staleStatePrevention.robot | minOnNoBindings.xml | /
MinOnGeneralTest | yes | pabot --pabotlib --processes 1 | Override_MinOnGeneral-test | MinOnGeneral | Reports | minOnGeneral.xml | config146 | General-test | minOnGeneralTest.robot | minOnGeneral.xml | /
combinereport | yes | rebot --removekeywords passed | Guard_Override_Test | Test performed across different environment and different group | Reports | basichotGuard.xml/deadSensorGuard.xml/hotGuard.xml/guardOrderMIX.xml/vxOverrideUIvalues.xml/uiPopup.xml/minOnNoBindings.xml/minOnGeneral.xml
moveReports | yes | robot |  |  | Reports/cleanReports | moveReports.xml | config118 |  | moveReports.robot
Note on O1: Do not change

## thursdaysuite
testcase | runmode | command | name | reporttitle | output dir | output | environment | groupname | testname | outputxml | slash | combineoutputxml
cleanReports | yes | robot |  |  | Reports/cleanReports | cleanReports.xml | config118 |  | cleanReports.robot |  |  | basichotGuard.xml/deadSensorGuard.xml/hotGuard.xml/guardOrderMIX.xml/vxOverrideUIvalues.xml/uiPopup.xml/minOnNoBindings.xml/minOnGeneral.xml
Guard1 | yes | pabot --pabotlib --processes 2 | Guard1_General-test | BasicHotAbsoluteGuard | Reports | basichotGuard.xml | config118 | General-test | basicHotAbsoluteGuardTest.robot/staleStatePrevention.robot | basichotGuard.xml
Guard2 | yes | pabot --pabotlib --processes 2 | Guard2_Imputes-test | DeadSensorGuard | Reports | deadSensorGuard.xml | config118 | Imputes-test | deadSensorGuardTest.robot/staleStatePrevention.robot | deadSensorGuard.xml | /
Guard3 | yes | pabot --pabotlib --processes 2 | Guard3_General-test | HotGuard | Reports | hotGuard.xml | config118 | General-test | hotGuardTest.robot/staleStatePrevention.robot | hotGuard.xml | /
Guard4 | yes | pabot --pabotlib --processes 2 | Guard4_General-test | GuardOrderMIX | Reports | guardOrderMIX.xml | config118 | General-test | guardOrderMIXTest.robot/staleStatePrevention.robot | guardOrderMIX.xml | /
Override1 | yes | pabot --pabotlib --processes 2 | Override1_General-test | VXOverrideUIvalues | Reports | vxOverrideUIvalues.xml | config118 | General-test | vxOverrideUIvaluesTest.robot/staleStatePrevention.robot | vxOverrideUIvalues.xml | /
UITestPopup | yes | pabot --pabotlib --processes 1 | Popup | Popups | Reports | uiPopup.xml | config118 | General-test | uiPopupTest.robot | uiPopup.xml | /
Override_minOnNoBindings | yes | pabot --pabotlib --processes 2 | Override_MinOnNoBindings-test | MinOnNoBindings | Reports | minOnNoBindings.xml | config146 | NoBindings | minOnNoBindingsTest.robot/staleStatePrevention.robot | minOnNoBindings.xml | /
MinOnGeneralTest | yes | pabot --pabotlib --processes 1 | Override_MinOnGeneral-test | MinOnGeneral | Reports | minOnGeneral.xml | config146 | General-test | minOnGeneralTest.robot | minOnGeneral.xml | /
combinereport | yes | rebot --removekeywords passed | Guard_Override_Test | Test performed on environment 118 | Reports | basichotGuard.xml/deadSensorGuard.xml/hotGuard.xml/guardOrderMIX.xml/vxOverrideUIvalues.xml/uiPopup.xml/minOnNoBindings.xml/minOnGeneral.xml
moveReports | yes | robot |  |  | Reports/cleanReports | moveReports.xml | config118 |  | moveReports.robot
Note on O1: Do not change

## commandinputdata
environment | groupname | guard1_name | guard2_name | guard3_name | guard4_name | Override1_name | runmode
config37 | General-test | Guard1_General-test | Guard2_General-test | Guard3_General-test | Guard4_General-test | Override1_General-test | yes
config64 | Imputes-test | Guard1_Imputes-test | Guard2_Imputes-test | Guard3_Imputes-test | Guard4_Imputes-test | Overide1_Imputes-test | no
config91 | RSP-test | Guard1_RSP-test | Guard2_RSP-test | Guard3_RSP-test | Guard4_RSP-test | Overide1_RSP-test
config118 | NoBindings
config146

## testexecutioncommands
testcase | commands to be executed from AuQA folder
CleanReports | sudo robot --outputdir Reports/cleanReports --output cleanReports.xml --variable environment:config37 /home/fc/automation/AuQA/Testcases/cleanReports.robot
Guard1 | sudo pabot --pabotlib --processes 2 --name 'Guard1_Imputes-test' --reporttitle "BasicHotAbsoluteGuard" --outputdir Reports --output basichotGuard.xml --variable environment:config37 -v groupname:Imputes-test -T /home/fc/automation/AuQA/Testcases/GuardTests/basicHotAbsoluteGuardTest.robot /home/fc/automation/AuQA/Testcases/staleStatePrevention.robot
Guard2 | sudo pabot --pabotlib --processes 2 --name 'Guard2_Imputes-test' --reporttitle "DeadSensorGuard" --outputdir Reports --output deadSensorGuard.xml --variable environment:config37 -v groupname:Imputes-test -T /home/fc/automation/AuQA/Testcases/GuardTests/deadSensorGuardTest.robot /home/fc/automation/AuQA/Testcases/staleStatePrevention.robot
Guard3 | sudo pabot --pabotlib --processes 2 --name 'Guard3_General-test' --reporttitle "HotGuard" --outputdir Reports --output hotGuard.xml --variable environment:config37 -v groupname:General-test -T /home/fc/automation/AuQA/Testcases/GuardTests/hotGuardTest.robot /home/fc/automation/AuQA/Testcases/staleStatePrevention.robot
Guard4 | sudo pabot --pabotlib --processes 2 --name 'Guard4_General-test' --reporttitle "GuardOrderMIX" --outputdir Reports --output guardOrderMIX.xml --variable environment:config37 -v groupname:General-test -T /home/fc/automation/AuQA/Testcases/GuardTests/guardOrderMIXTest.robot /home/fc/automation/AuQA/Testcases/staleStatePrevention.robot
Override1 | sudo pabot --pabotlib --processes 2 --name 'Override1_General-test' --reporttitle "VXOverrideUIvalues" --outputdir Reports --output vxOverrideUIvalues.xml --variable environment:config37 -v groupname:General-test -T /home/fc/automation/AuQA/Testcases/OverrideTests/vxOverrideUIvaluesTest.robot /home/fc/automation/AuQA/Testcases/staleStatePrevention.robot
UITestPopup | sudo robot --name 'Popup' --reporttitle "Popups" --outputdir Reports --output uiPopup.xml --variable environment:config37 -v groupname:General-test -T /home/fc/automation/AuQA/Testcases/UITests/uiPopupTest.robot
Override_MinOnNoBindings-test | sudo pabot --pabotlib --processes 2 --name 'Override_MinOnNoBindings-test' --reporttitle "MinOnNoBindings" --outputdir Reports --output minOnNoBindings.xml --variable environment:config146 -v groupname:NoBindings -T /home/fc/automation/AuQA/Testcases/OverrideTests/minOnNoBindingsTest.robot /home/fc/automation/AuQA/Testcases/staleStatePrevention.robot
Override_MinOnGeneral-test | sudo robot --name 'Override_MinOnGeneral-test' --reporttitle "MinOnGeneral" --outputdir Reports --output minOnGeneral.xml --variable environment:config146 -v groupname:General-test /home/fc/automation/AuQA/Testcases/OverrideTests/minOnGeneralTest.robot
CombineReports | sudo rebot --removekeywords passed --name 'Guard_Override_Test' --reporttitle "Test performed on environment 37" --outputdir Reports --output output.xml /home/fc/automation/AuQA/Reports/basichotGuard.xml /home/fc/automation/AuQA/Reports/deadSensorGuard.xml /home/fc/automation/AuQA/Reports/hotGuard.xml /home/fc/automation/AuQA/Reports/guardOrderMIX.xml /home/fc/automation/AuQA/Reports/vxOverrideUIvalues.xml /home/fc/automation/AuQA/Testcases/UITests/uiPopup.xml /home/fc/automation/AuQA/Testcases/OverrideTests/minOnNoBindingsTest.robot /home/fc/automation/AuQA/Testcases/OverrideTests/minOnGeneralTest.robot
MoveReports | sudo robot --outputdir Reports/cleanReports --output moveReports.xml --variable environment:config37 /home/fc/automation/AuQA/Testcases/moveReports.robot
SendEmail | sudo python3 ExternalKeywords/sendemail.py <name of the suite executed> e.g. sudo python3 ExternalKeywords/sendemail.py thursdaysuite
suitename | suite execution commands
tuesdayexecutesuite | sudo chmod 775 tuesdayexecutesuite.sh sudo sh tuesdayexecutesuite.sh
wednesdayexecutesuite | sudo chmod 775 wednesdayexecutesuite.sh sudo sh wednesdayexecutesuite.sh
thursdayexecutesuite | sudo chmod 775 thursdayexecutesuite.sh sudo sh thursdayexecutesuite.sh

## uitest
popups | popuptitle/popupmessage
suppress_alarm_popup_title | Suppress Alarm
suppress_alarm_popup_message | Please select an alarm first.
selected_suppress_alarm_popup_message | Suppress notifications for the selected alarm?
suppressed_alarm_popup_title | Suppressed Alarms
restore_suppressed_alarm_title | Restore Suppressed Alarm
restore_all_suppressed_alarms_title | Restore All Suppressed Alarms
restore_all_suppressed_alarms_message | Restore notifications for all alarms?
set_overrides_popup_title | Set Overrides
set_overrides_popup_message | Select equipment to override.
clear_overrides_popup_title | Clear Overrides
clear_overrides_popup_message | Select equipment to clear.
show_trends_popup_title | Show Trends
show_trends_popup_message | No equipment selected.
bypass_popup_title | Bypass Control Group
bypass_popup_message | Note: AHUs will be set to maximum cooling in random order. This will occur over 300 seconds. Existing manual overrides will not be affected. Override all equipment for group General-test to the configured maximum cooling level?
dustmotelinepower_popup_message | Alarm subject 00-17-0D-00-00-1A-C8-A0 is not bound to any assets.
dustmotelinepower_popup_title | DustMoteLinePower 00-17-0D-00-00-1A-C8-A0
validation_error_popup_title | Validation Error
sfcmin_popup_message | SYSTEM.SFCMin: The value must not be blank.
save_popup_title | Save
save_popup_message | Nothing to save.
turn_off_limit_24_hr_popup_message | DASHM.TurnOffLimit24H: The unsigned integer is below the minimum of 0
unsaved_changes_popup_title | Unsaved Changes
unsaved_changes_popup_message | Discard changes before closing this window?