## guardTest
basicHotAbsoluteGuardInputs | values | deadSensorGuardInputs | values | hotGuardTestInputs | values | guardOrderMIXInputs | values
num_guard_units | 1 | ds_num_guard_units_value | 1 | config_allow_num_exceedences_guard_initial | 1 | fan_ctlr_min_value | 50
num_minutes_guard_timer | 3 | ds_num_minutes_guard_timer_value | 2 | config_allow_num_exceedences_guard_value2 | 2 | fan_ctrl_max_value | 100
percent_deadsensor_threshold | 100 | ds_percent_dead_sensor_threshold_default_value | 30 | group_allow_num_exceedences_guard_value0 | 0 | allow_num_exceedences_guard_cleanup_value | 9
num_minutes_past | 5 | ds_num_minutes_past_value | 2 | group_allow_num_exceedences_guard_value1 | 1 | guard_hot_abs_temp_cleanup_value | 95
allow_num_exceedences_control_initial | 10 | dead_sensor_test_temp | 66 | group_allow_num_exceedences_guard_value2 | 2 | allow_num_exceedences_control_cleanup_value | 9
allow_num_exceedences_guard_initial | 10 | alarm_dead_sensor_hysteresis_cleanup_value | 0 | config_CAT_guard_band_range_initial | 4 | guard_hot_abs_temp_intial | 99
alm_hot_abs_temp_initial | 200 | alarm_dead_sensor_threshold_cleanup_value | 0 | config_CAT_guard_band_range_value5 | 5 | rack_temp | 66
guard_hot_abs_temp_intial | 90 | control_dead_sensor_threshold_cleanup_value | 0 | config_num_guard_units_value1 | 1 | high_set_point_limit | 80.6
allow_num_exceedences_control_default | 0 | dead_sensor_alarm_count | 1 | config_num_guard_units_value2 | 2 | high_set_point_limit_cleanup | 88
allow_num_exceedences_guard_default | 1 | guard_on | GUARD_ON | config_num_minutes_guard_timer_value2 | 2 | low_set_point_limit | 64.4
alm_hot_abs_temp_default | 90 | guard_off | GUARD_OFF | config_num_minutes_guard_timer_value4 | 4 | low_set_point_limit_cleanup | 60
guard_hot_abs_temp_default | 90 | group_dead_sensor_alarm_on | ALARM_ON | config_guard_hysteresis_band_value1 | 1 | config_num_guard_units_value | 1
percent_deadsensor_threshold_default | 30 | group_dead_sensor_alarm_off | ALARM_OFF | config_guard_hysteresis_band_value2 | 2 | config_num_minutes_guard_timer_value | 1
sensor_point_cooling_temp | 65 | control_dead_sensor_threshold_property_name | ControlDeadSensorThreshold | high_set_point_limit | 80.6 | config_system_num_minutes_past | 20
sensor_point_hot_temp | 100 | grp_dead_sensor_hysteresis_value_default_value | 10 | high_set_point_limit_cleanup | 88 | first_ahus_predicted_into_guard | CAC_16,CAC_13,CRAC_3A-02
expected_ahu_to_be_on | 4 |  |  | low_set_point_limit | 64.4 | CAC_10 | 70
|  |  |  | low_set_point_limit_cleanup | 60 | CAC_11 | 100
|  |  |  | guard_on | GUARD_ON | CAC_12 | 90
|  |  |  | guard_off | GUARD_OFF | CAC_13 | 80
|  |  |  | group_hot_alarm_on | ALARM_ON | CAC_14 | 66
|  |  |  | group_hot_alarm_off | ALARM_OFF | CAC_15 | 60
|  |  |  | allow_num_exceedences_guard_cleanup_value | 9 | CAC_16 | 50
|  |  |  | guard_hot_abs_temp_cleanup_value | 99 | CAC_17 | 75
|  |  |  | alm_hot_abs_temp_cleanup_value | 99 | CRAC_3A-01 | 100
|  |  |  | hot_guard_intial_temp_all_racks | 66 | CRAC_3A-02 | 50
[6 empty] | CRAC_3A-03 | 80
[6 empty] | CRAC_3A-04 | 70

## tuesdaysuite
runmode | testcase | command | name | reporttitle | output dir | output | environment | groupname | testname
| cleanReports | robot |  |  | Reports/cleanReports | cleanReports.xml | config146 |  | cleanReports.robot
No | Guard1 | pabot --pabotlib --processes 2 | Guard1_Imputes-test | BasicHotAbsoluteGuard | Reports | basichotGuard.xml | config146 | Imputes-test | basicHotAbsoluteGuardTest.robot/staleStatePrevention.robot
Yes | Guard2 | pabot --pabotlib --processes 2 | Guard2_Imputes-test | DeadSensorGuard | Reports | deadSensorGuard.xml | config146 | Imputes-test | deadSensorGuardTest.robot/staleStatePrevention.robot
Yes | Guard3 | pabot --pabotlib --processes 2 | Guard3_General-test | HotGuard | Reports | hotGuard.xml | config146 | General-test | hotGuardTest.robot/staleStatePrevention.robot
Yes | Guard4 | pabot --pabotlib --processes 2 | Guard4_General-test | GuardOrderMIX | Reports | guardOrderMIX.xml | config146 | General-test | guardOrderMIXTest.robot/staleStatePrevention.robot
| combinereport | rebot --removekeywords passed | Override_Test | Test performed on environment 37 | Reports | deadSensorGuard.xml/hotGuard.xml/guardOrderMIX.xml
| moveReports | robot |  |  | Reports/cleanReports | moveReports.xml | config146 |  | moveReports.robot

## thursdaysuite
runmode | testcase | command | name | reporttitle | output dir | output | environment | groupname | testname
| cleanReports | robot |  |  | Reports/cleanReports | cleanReports.xml | config118 |  | cleanReports.robot
Yes | Guard1 | pabot --pabotlib --processes 2 | Guard1_General-test | BasicHotAbsoluteGuard | Reports | basichotGuard.xml | config118 | General-test | basicHotAbsoluteGuardTest.robot/staleStatePrevention.robot
Yes | Guard2 | pabot --pabotlib --processes 2 | Guard2_Imputes-test | DeadSensorGuard | Reports | deadSensorGuard.xml | config118 | Imputes-test | deadSensorGuardTest.robot/staleStatePrevention.robot
No | Guard3 | pabot --pabotlib --processes 2 | Guard3_General-test | HotGuard | Reports | hotGuard.xml | config118 | General-test | hotGuardTest.robot/staleStatePrevention.robot
Yes | Guard4 | pabot --pabotlib --processes 2 | Guard4_General-test | GuardOrderMIX | Reports | guardOrderMIX.xml | config118 | General-test | guardOrderMIXTest.robot/staleStatePrevention.robot
| combinereport | rebot --removekeywords passed | Override_Test | Test performed on environment 118 | Reports | basichotGuard.xml/deadSensorGuard.xml/guardOrderMIX.xml
| moveReports | robot |  |  | Reports/cleanReports | moveReports.xml | config118 |  | moveReports.robot

## wednesdaysuite
runmode | testcase | command | name | reporttitle | output dir | output | environment | groupname | testname
| cleanReports | robot |  |  | Reports/cleanReports | cleanReports.xml | config118 |  | cleanReports.robot
Yes | Guard1 | pabot --pabotlib --processes 2 | Guard1_RSP-test | BasicHotAbsoluteGuard | Reports | basichotGuard.xml | config37 | RSP-test | basicHotAbsoluteGuardTest.robot/staleStatePrevention.robot
No | Guard2 | pabot --pabotlib --processes 2 | Guard2_Imputes-test | DeadSensorGuard | Reports | deadSensorGuard.xml | config91 | Imputes-test | deadSensorGuardTest.robot/staleStatePrevention.robot
Yes | Guard3 | pabot --pabotlib --processes 2 | Guard3_General-test | HotGuard | Reports | hotGuard.xml | config118 | General-test | hotGuardTest.robot/staleStatePrevention.robot
No | Guard4 | pabot --pabotlib --processes 2 | Guard4_General-test | GuardOrderMIX | Reports | guardOrderMIX.xml | config118 | General-test | guardOrderMIXTest.robot/staleStatePrevention.robot
| combinereport | rebot --removekeywords passed | Override_Test | Test performed across different environment and different group | Reports | basichotGuard.xml/hotGuard.xml
| moveReports | robot |  |  | Reports/cleanReports | moveReports.xml | config118 |  | moveReports.robot

## commandinputdata
environment | groupname | guard1_name | guard2_name | guard3_name | guard4_name | Yes/No | wednesdaysuite |  | basichotGuard.xml/hotGuard.xml | thursdaysuite |  | basichotGuard.xml/deadSensorGuard.xml/guardOrderMIX.xml | tuesdaysuite |  | deadSensorGuard.xml/hotGuard.xml/guardOrderMIX.xml | tuesdaysuitecombinetestname | thursdaysuitesuitecombinetestname | wednesdaysuitecombinetestname
config37 | General-test | Guard1_General-test | Guard2_General-test | Guard3_General-test | Guard4_General-test | Yes | runmode | slash |  | runmode | slash |  | runmode | slash |  | name | name | name
config64 | Imputes-test | Guard1_Imputes-test | Guard2_Imputes-test | Guard3_Imputes-test | Guard4_Imputes-test | No | basichotGuard.xml |  |  | basichotGuard.xml | [5 empty] | Guard_Test | Guard_Test | Guard_Test
config91 | RSP-test | Guard1_RSP-test | Guard2_RSP-test | Guard3_RSP-test | Guard4_RSP-test |  |  |  |  | deadSensorGuard.xml | / |  | deadSensorGuard.xml |  |  | Guard_Test | Guard_Test | Guard_Test
config118 | [6 empty] | hotGuard.xml | / |  |  |  |  | hotGuard.xml | / |  | Override_Test | Override_Test | Override_Test
config146 | [9 empty] | guardOrderMIX.xml | / |  | guardOrderMIX.xml | /

## testexecutioncommands
testcase | commands
Guard1 | pabot --pabotlib --processes 2 --name "Guard1_RSP-test_$(date +%F_%H:%M:%S)" --reporttitle "BasicHotAbsoluteGuard" --outputdir Reports --output basichotGuard.xml --variable environment:config37 -v groupname:RSP-test --removekeywords passed
Guard2 | pabot --pabotlib --processes 2 --name "Guard2_Imputes-test_$(date +%F_%H:%M:%S)" --reporttitle "DeadSensorGuard" --outputdir Reports --output deadSensorGuard.xml --variable environment:config37 -v groupname:Imputes-test --removekeywords passed
Guard3 | pabot --pabotlib --processes 2 --name "Guard3_General-test_$(date +%F_%H:%M:%S)" --reporttitle "HotGuard" --outputdir Reports --output hotGuard.xml --variable environment:config37 -v groupname:General-test --removekeywords passed
Guard4 | pabot --pabotlib --processes 2 --name "Guard4_General-test_$(date +%F_%H:%M:%S)" --reporttitle "GuardOrderMIX" --outputdir Reports --output guardOrderMIX.xml --variable environment:config37 -v groupname:General-test --removekeywords passed